WATER QUALITY REPORT

Borehole water assessment at Dr. Timbo's Residence, Western Area Rural District

Client: Dr. Timbo

Sample ID: WQ-BH1-01

Borehole: BH-1

Sample date: 20th May, 2018

Laboratory: Example Laboratory, Freetown

PROVISIONAL - NOT FOR CERTIFICATION

This report rests on incomplete results. The following requirements for certification are outstanding.

Field data: Readings that were never measured are in this project: dr_timbo_water_quality.xlsx. The values in that file were invented to demonstrate the toolkit, so no result derived from them describes anything that was sampled.

Site position: No GPS position is recorded on any sheet in this project. A borehole that cannot be found again on the ground cannot be certified, revisited or maintained.

# Executive Summary

This report is provisional and not a certification (outstanding: Field data, Site position). The findings below are those the supplied records support; the cover says what is missing.

Laboratory results for the borehole water at Dr. Timbo's Residence were assessed against the WHO Guidelines for Drinking-water Quality and the national/adopted limits. The water does not meet the health based guideline value for Manganese, so treatment or an alternative source is required before it is used for drinking. The water also fails the national standard limit for Total coliforms.

Key findings:

Health based exceedance: Manganese.

National standard exceedance: Total coliforms.

Treatment or an alternative source is required before drinking.

# 1. Sample Details

| Community | Dr. Timbo's Residence | Client | Dr. Timbo |
| --- | --- | --- | --- |
| Sample ID | WQ-BH1-01 | Borehole Ref. No. | BH-1 |
| Sample date | 20th May, 2018 | Laboratory | Example Laboratory, Freetown |
| District | Western Area Rural | Project | Borehole completion |

Results are compared against the WHO Guidelines for Drinking-water Quality (fourth edition with addenda) and the national standard limits configured for this project. Where a confirmed national value is not available, the WHO or regional figure is adopted for that parameter and the status column reads national/adopted limit. Values reported by the laboratory as below the detection limit are shown as such.

The national column in the standards table is provisional: its values are WHO guideline figures carried across, or limits adopted from regional practice, and have not been confirmed against the Sierra Leone Standards Bureau drinking water specification. Confirm the figures before treating a national exceedance as a compliance finding.

## 1.1 Location and setting

The site is recorded as Dr. Timbo's Residence, Western Area Rural district. No GPS position is recorded for it, so the maps below cover Western Area Rural district rather than the borehole itself and carry no site marker. Record the position on the field sheet and reissue this report: a borehole that cannot be found again on the ground cannot be revisited or maintained.

Figure 1. Study area at Western Area Rural district, with its location in Sierra Leone inset. Boundaries from geoBoundaries (CC BY 4.0).

Figure 2. Location of Western Area Rural district. Boundaries from geoBoundaries (CC BY 4.0).

# 2. Results Against Guideline Values

Table 1 lists every parameter tested. Exceedances are highlighted in the status column.

Table 1. Laboratory results against guideline values.

| Parameter | Value | Unit | WHO health | WHO acceptability | National | Status |
| --- | --- | --- | --- | --- | --- | --- |
| pH | 5.9 | pH units |  | 6.5-8.5 | 6.5-8.5 | Exceeds acceptability value |
| Electrical conductivity | 185 | uS/cm |  |  | 2500 | Complies |
| TDS | 120 | mg/L |  | 1000 | 1000 | Complies |
| Turbidity | 3.2 | NTU |  |  | 5 | Complies |
| Temperature | 27.4 | deg C |  |  |  | No guideline value |
| Total hardness | 58 | mg/L as CaCO3 |  |  | 500 | Complies |
| Alkalinity | 46 | mg/L as CaCO3 |  |  |  | No guideline value |
| Calcium | 14.2 | mg/L |  |  |  | No guideline value |
| Magnesium | 5.5 | mg/L |  |  |  | No guideline value |
| Sodium | 12.6 | mg/L |  | 200 | 200 | Complies |
| Potassium | 2.1 | mg/L |  |  |  | No guideline value |
| Bicarbonate | 56 | mg/L |  |  |  | No guideline value |
| Chloride | 18.4 | mg/L |  | 250 | 250 | Complies |
| Sulfate | 6.8 | mg/L |  | 250 | 250 | Complies |
| Nitrate (as NO3) | 8.2 | mg/L | 50 |  | 50 | Complies |
| Nitrite (as NO2) | < DL | mg/L | 3 |  | 3 | Below detection |
| Ammonia (as N) | 0.12 | mg/L |  | 1.5 | 1.5 | Complies |
| Fluoride | 0.22 | mg/L | 1.5 |  | 1.5 | Complies |
| Iron | 0.85 | mg/L |  | 0.3 | 0.3 | Exceeds acceptability value |
| Manganese | 0.12 | mg/L | 0.08 | 0.1 | 0.08 | EXCEEDS HEALTH GUIDELINE |
| Arsenic | < DL | mg/L | 0.01 |  | 0.01 | Below detection |
| Lead | < DL | mg/L | 0.01 |  | 0.01 | Below detection |
| Copper | 0.02 | mg/L | 2 | 1 | 2 | Complies |
| Zinc | 0.11 | mg/L |  | 3 | 3 | Complies |
| Chromium (total) | < DL | mg/L | 0.05 |  | 0.05 | Below detection |
| Cadmium | < DL | mg/L | 0.003 |  | 0.003 | Below detection |
| E. coli | 0 | CFU/100 mL | 0 |  | 0 | Complies |
| Total coliforms | 4 | CFU/100 mL |  | 0 | 0 | Exceeds national/adopted limit |

The water does not meet the health based guideline value for: Manganese. Treatment or an alternative source is required before the water is used for drinking.

Water Quality Index: 224 (Very poor), over 10 physico-chemical parameters.

Health Hazard Index: 0.19 (Acceptable (Hazard Index below 1)).

# 3. Ionic Balance Check

Sum of cations 1.8 meq/L, sum of anions 1.72 meq/L, charge balance error +2.1 percent. The analysis balances within the normal 5 percent tolerance.

# 4. Corrosivity and Materials

The water is chemically aggressive (Ryznar index 11.4, Langelier index -2.7). It will corrode metal fittings. The pH of 5.9 is below the 6.5 to 8.5 acceptability range, which adds to the attack on metal; soft, low-alkalinity basement groundwater is aggressive even at a pH inside that range.

Table 2. Corrosivity and scaling indices.

| Index | Value |
| --- | --- |
| Langelier Saturation Index (LSI) | -2.74 |
| Ryznar Stability Index (RSI) | 11.37 |
| Aggressive Index (AI) | 9.11 |
| Larson-Skold ratio | 0.72 |
| Classification | Strongly corrosive |

Specify uPVC or stainless steel (grade 304 or 316) for the rising main and pump components, and avoid galvanised iron and mild steel, which corrode rapidly in this water and are a leading cause of premature pump failure. Inspect the rising main and the wetted metal parts of the pump for corrosion at each service.

# 5. Hydrochemical Facies

The water is a mixed-cation-HCO3 type (Ca 40%, Mg 26%, Na+K 34%; HCO3 58%, Cl 33%, SO4 9%, in milliequivalent percent): a bicarbonate water with no single dominant cation, in which calcium and magnesium together still outweigh sodium and potassium; a fresh water of the kind weathering of silicate rock gives, with the sodium share pointing to feldspar weathering or some ion exchange along the flow path.

Figure 3. Piper diagram: the sample's major-ion composition, with the cations on the left triangle, the anions on the right and the combined point in the diamond.

Figure 4. Stiff diagram: the same composition as a shape, cations to the left and anions to the right of the axis.

# 6. Recommendations

Specify uPVC or stainless steel (grade 304 or 316) for the rising main and pump components, and avoid galvanised iron and mild steel, which corrode rapidly in this water and are a leading cause of premature pump failure. Inspect the rising main and the wetted metal parts of the pump for corrosion at each service.

Treat or replace the source before it is used for drinking: health based limits are exceeded for Manganese.

Treat before the supply is accepted against the national standard: national limits are exceeded for Total coliforms.

Manganese requires oxidation and filtration (aeration or chlorination followed by filtration); monitor infant exposure in the meantime.

Coliform detection calls for disinfection of the borehole and pump, a sanitary inspection of the wellhead, and re-sampling.

Low pH water is corrosive to metal fittings; a limestone contactor or careful choice of corrosion resistant materials is advised.

Iron above the acceptability value causes staining and metallic taste; aeration followed by sand filtration or a simple oxidation filter normally resolves it.

Acceptability limits are exceeded for pH, Iron: simple treatment is advisable if users complain of taste, odour or staining.

Disinfect the borehole after any maintenance and re-test microbiological quality before the source is returned to use.

Repeat physico-chemical and bacteriological testing at least once a year, and after any flooding, repair work on the wellhead or change in taste, colour or odour.

# 7. Limitations and Uncertainty

The results describe a single sample at one point in time. Water quality varies with the season, rainfall and the condition of the wellhead, so periodic re-testing is needed to confirm the verdict.

Parameters reported below the laboratory detection limit are shown as such; a non-detection does not prove complete absence.

The corrosivity and index calculations use the parameters supplied. Missing pH, calcium or alkalinity limit what can be assessed, and any assumptions made are stated where they are used.

# References

World Health Organization (2022). Guidelines for Drinking-water Quality, 4th edition incorporating the first and second addenda. Geneva: World Health Organization.

Sierra Leone Standards Bureau. Sierra Leone Standard for drinking water quality (SLS). Freetown: SLSB. Edition and date not verified against the issued specification: the national limits this toolkit applies are provisional (WHO or regional figures carried across) until confirmed against it.

Langelier, W.F. (1936). The analytical control of anti-corrosion water treatment. Journal of the American Water Works Association, 28, 1500-1521.

# Glossary and Abbreviations

| Term | Meaning |
| --- | --- |
| VES | Vertical electrical sounding, a resistivity depth survey |
| AB/2 | Half the current-electrode spacing in a Schlumberger array |
| ohm-m | Ohm-metre, the unit of electrical resistivity |
| ERR | Root-mean-square misfit of the fitted layered model (percent) |
| S (Dar-Zarrouk) | Longitudinal conductance, sum of thickness/resistivity (siemens) |
| T (Dar-Zarrouk) | Transverse resistance, sum of thickness x resistivity (ohm m2) |
| SWL | Static water level, the rest water level before pumping |
| DWL | Dynamic water level, the water level during pumping |
| T (transmissivity) | Aquifer transmissivity (m2/day) |
| S (storativity) | Aquifer storage coefficient (dimensionless) |
| m3/h | Cubic metres per hour, a discharge or yield rate |
| LSI / RSI | Langelier and Ryznar indices of water corrosivity and scaling |
| WQI | Water Quality Index, an aggregate 0-based quality score |
| HI | Health Hazard Index, the sum of chronic hazard quotients |
| uPVC | Unplasticised polyvinyl chloride, the casing and screen material |
| GPS / UTM | Satellite positioning and the Universal Transverse Mercator grid |
| WASH | Water, sanitation and hygiene |
| RWSN | Rural Water Supply Network |
| SALWACO | Sierra Leone Water Company |
| WHO | World Health Organization |
| SLSB | Sierra Leone Standards Bureau |

REPORT SUBMITTED BY:

..............................

Water Quality Analyst